AccuMax Fury 40GPM Detailed Specifications

A FoamPro AccuMax Fury, part number MAX040-Fury electronic/hydraulic foam proportioning system shall be provided. The system shall be demand-based, fully automatic and shall be compatible with all current foam concentrates. All of the electronics shall be EMI/RFI compliant. The foam proportioning operation shall be based on direct measurement of water flow and shall remain consistent within the specified flows and pressures. The system shall be capable of accurately delivering foam solution as required by applicable sections of NFPA standards. The system shall be capable of accurately delivering foam solution to within 5% of calibrated settings over the advertised operation range when installed in the apparatus. The foam system shall be able to control up to fifteen (15) different foam capable discharges. Each foam capable discharge shall allow the choice of plain water, 0.1% through 10% foam solution; with the percentage chosen by the operator in 0.1% increments.

A main waterway check valve shall be available as an option. The individual line controller manages concentrate injection, continuously monitoring performance and feeds the hydraulic control (XE-MAX120-D0A) with information and requirements. The hydraulic control totals concentrate requirements and directs the rotary gear pump to perform accordingly.
All electronic control modules shall be suitable for mounting on a fire truck operator panel. Water flow measurement of each foam capable discharge shall be accomplished by a non-restricting flowmeter and shall be of paddlewheel or magnetic meter design. Devices placed in the discharge piping that restrict water flow and reduce nozzle performance shall not be acceptable. All system components shall be constructed of non-corrosive materials. To prevent waste of costly foam concentrate, the system shall allow calibration and performance testing without mixing concentrate with water.

Individual Line Controllers (Panel Display) 
A microprocessor equipped individual line controller shall be provided for each foam capable discharge. It shall include’ an ultra-bright sun-readable LCD display for maximum readability. The display shall allow the pump operator to perform the following control and operation functions for each discharge:
•	Choose between plain water or foam solution
•	Provide pushbutton control of foam proportioning rates
•	Display current flow-per-minute of water
•	Display total volume of water discharged during and after foam operations 
are completed
•	Display total amount of foam concentrate consumed
•	Display injection percentage
•	Simulate flow rates for manual operation
•	Perform setup and diagnostic functions 
•	Allow up to nine (9) injection percentage defaults to be stored

Additional overall system information (viewed from any display)
•	Display total current flow-per-minute of water
•	Display total volume of water discharged during and after foam operations 
are completed
•	Show total amount of foam concentrate consumed
•	Flash a “SYS. LOW FOAM” warning when the foam concentrate tank runs low
•	Flash a “SYS. NO FOAM SHUTDOWN” warning and shut off the foam concentrate pump, preventing damage to the pump, should the foam tank 
become empty
•	Perform setup and diagnostic functions
•	Provides time remaining warning until tank is empty when used with TankvisonPro 

Hydraulic System
The hydraulic piston pump shall be variable displacement to provide longer life and reduce service. Hydraulic gear pumps shall not be acceptable. The hydraulic system shall comply with all applicable SAE and DOT standards. The hydraulic system shall have an oil cooler and an appropriately sized hydraulic reservoir to maintain the temperature of the hydraulic oil at or below 220°F (104°C).

Concentrate Pump
The all bronze rotary gear concentrate pump shall be produced and supplied by Fire Lion or Trident Titan. The foam pump shall be capable of running dry and pumping water at full performance levels without causing pump damage. A hydraulic motor driven positive displacement foam concentrate pump shall be provided and installed in an accessible location. The pump capacity range shall be 2 GPM (7.57 L/min) to 40 GPM (151.4 L/min) with maximum operating pressure of 300 PSI (20.7 BAR). An electronically-operated valve shall receive signals from the hydraulic control to monitor the flow of hydraulic oil to the hydraulic motor coupled to the concentrate pump. The concentrate pump turns at a variable speed to ensure that the correct proportion of concentrate selected by the pump operator is injected into the fire pump discharge stream. 

Base System Components
•	Hydraulic Controller 
•	Fire Lion, Trident or Edwards Manufacturing concentrate pump coupled to hydraulic motor
•	Variable displacement piston hydraulic pump
•	Foam relief valve
•	Pressure transducer
•	Foam flowmeter
•	Foam level indicator/sensor
•	Strainer
•	Molded cables

Individual Line Discharge Components
•	Individual line controller with sun-readable LCD and over molded button 
•	Foam flowmeter and valve with integrated controls assembly
•	Molded cables (carrying power, ground and data bus single) 
•	Water flowmeter
•	Injection Check valve
•	Calibrate/Inject valve

To prevent waste of costly foam concentrate and environmental concerns, the system shall allow calibration and performance testing with water only, or without mixing concentrate with water. The foam system shall be installed and calibrated to manufacturer's requirements. In addition, the system shall be tested and certified by the apparatus manufacturer to applicable NFPA standards. Two (2) installation and operation manuals shall be provided with the unit. The system shall have a two (2) year warranty by the foam system manufacturer.

Line Control 

Note:  line controllers shall be based upon the system configuration, and the appropriate line controller size shall be chosen for the size of the system.

(From the information below, please select the quantity and size(s) Foam line Injector according to your specific foam system configuration.)

1/2" Ultra-Wide Range Foam Line Controller (FLI- Foam Line Injector) 
A FoamPro individual line controller with microprocessor shall be provided for each specified foam capable discharge below. Each controller shall include an ultra-bright sun-readable LCD display for maximum readability. The foam line controllers shall have a connection to each foam flowmeter and provide concentrate flow from 1.0 GPM 
(3.7 L/min) to 26 GPM (98.4 L/min). The displays shall allow the pump operator to perform the control and operation functions for each discharge.

1" Ultra-Wide Range Foam Line Controller (FLI- Foam Line Injector)
A FoamPro individual line controller with microprocessor shall be provided for each specified foam capable discharge below. Each controller shall include an ultra-bright LED digital display for maximum readability. The foam line controllers shall have a connection to each foam flowmeter and provide concentrate flow from 2.0 GPM (6.8L/min) to 60 GPM (227.1 L/min). The displays shall allow the pump operator to perform the control and operation functions for each discharge.

Low Flow Line 
A FoamPro Low-Flow Line Injector shall be provided to deliver precision proportioning for low flow applications that may be required below the normal operating range of the foam pump as specified. Operation shall be integrated into system hydraulic controller and deliver seamless, automatic adjustments to flow conditions without 
operator interface.